Calculation programme for the operation of open recooling plants and air scrubbers
Status 01/2016

## Contents

Page

1.  Basics												2

1.1 Raw water analysis										3

1.2 Window for entering the kind of system								5

2.  Calculation of thickening and circulating water quality in the cooling tower circuit	5

2.1 Cooling tower circuit input screen								6

2.1.1. Threshold stabilisation									8

2.1.2. Softening and threshold stabilisation								8

2.1.3. Decarbonisation and threshold stabilisation							9

2.1.4. Desalination via reverse osmosis with softening and threshold stabilisation			9

2.1.5. Desalination via reverse osmosis without softening and threshold stabilisation 			9

2.1.6. Sulphuric acid dosing and threshold stabilisation						10

2.2. Correction of electrical conductivity								10

- Calculation of thickening and circulating water quality in the air scrubber			11

3.1     Air scrubber input mask									11

3.1.1. Threshold stabilisation									12

3.1.2. Softening and threshold stabilisation								12

3.1.3. Decarbonisation and threshold stabilisation							12

3.1.4. Desalination via reverse osmosis with softening and threshold stabilisation			13

3.1.5. Desalination via reverse osmosis without softening and threshold stabilisation 			13

- Operating cost calculation input mask							13

4.1.1. Threshold stabilisation									14

4.1.2. Softening and threshold stabilisation								14

4.1.3. Decarbonisation and threshold stabilisation							14

4.1.4. Desalination via reverse osmosis with softening and threshold stabilisation			15

4.1.5. Desalination via reverse osmosis without softening and threshold stabilisation 			15

4.1.6. Sulphuric acid dosing and threshold stabilisation						15

- Further programme options									16

5.1.   System information										16

5.2.1.Open file											16

5.2.2 Save file as											16

5.2.3 Import/export file										16

5.2.4.Print file											16

5.3.   Edit language										16

## Evaporation cycles

##### The operation of cooling tower plants and air scrubbers

1	Fundamentals

The fundamental questions for the operation of evaporation cycles are always: How must operating water for such systems be treated and conditioned in order to achieve optimum operational safety and service life at minimum cost?

Relevant guidelines provide a framework for the quality of operating water and the maintenance of the systems. In particular, these are the current versions of:

42. BImSchV Ordinance on evaporative cooling systems, cooling towers and wet separators

VDI 2047 Sheet 2 Recooling plants – Ensuring hygienic operation of evaporative cooling systems (VDI cooling tower rules).

VDI 6022 (all sheets) Hygienic requirements for ventilation and air conditioning systems;

VDMA 24649 Information and recommendations for the safe operation of evaporative cooling systems
VDMA 24186 Service programme for the maintenance of technical systems and equipment in buildings Part 3: Refrigeration equipment and systems for cooling and heating purposes;

VDI 3803 Ventilation and air conditioning systems – Structural and technical requirements.

This programme is a powerful tool for performing the complex calculations required for the operation of recooling plants (RKW) and air washers (LW) for the treatment and processing of different make-up water qualities. Its performance is unique to date.

It is also intended to help planners of industrial cooling plants and air conditioning systems to take into account the necessary plant technology for the treatment of feed water for recooling plants and air scrubbers. However, it cannot replace the expertise of specialists in industrial and commercial water treatment.

A description of the algorithms used in the individual programmes provides the best information about the possibilities and limitations of this tool. It becomes clear that, in addition to physical and chemical laws, recognised guidelines and recommendations from the authors are also incorporated into the programme structures.

The main focus of the calculations for cooling tower circuits is to ensure that operation is free of mineral deposits, especially calcium carbonate deposits. The avoidance of increased corrosion of the circulating water is covered by various limiting conditions. The 42nd BImSchV, as well as the guidelines VDI 2047 Sheet 2 and VDI 3803, can be taken into account as criteria for circulating water quality. Product selection with regard to the best possible corrosion protection is not the subject of this programme.

  - Raw water analysis

The operating costs of a recooling plant (RKW) are mainly determined by the costs for additional water and the fees for the discharge of wastewater. In evaporative cooling systems, the amount of evaporation water is a linear function of the amount of heat to be removed. The decisive cost factor for a given cooling capacity is therefore the amount of wastewater resulting from the thickening factor E, at which deposit-free operation and good corrosion protection can be guaranteed.

In order to keep water and wastewater costs low, an appropriately high thickening factor must be achieved. This depends on the feed water quality. The feed water is produced from raw water. The raw water quality is essentially characterised by the following parameters, which are specified via the input mask.

Input parameters:

Extraction temperature TE	This is not relevant for the operating conditions in the RKW or air scrubber (LW), but is required to calculate the saturation index (SI) in order to assess the tendency to form deposits and the material behaviour in make-up water pipes. Water supply companies are required to provide drinking water with an SI close to 0.0.

Electrical conductivity (25 °C)	The measured value to be entered is compared with the calculated value based on the equivalent conductivities of the entered ion concentrations and the Debye-Hückel-Onsager correction. The difference between the sum of anions and the sum of alkaline earth metals is reported as sodium. If no value for nitrate has been entered, the positive difference between the measured and calculated conductivity is calculated as sodium nitrate. If the difference is negative and the deviation is greater than 15%, a message indicating poor measurements is displayed ( ). For values above 2000 µS/cm in raw water, the method becomes increasingly inaccurate, but is still possible and helpful.

Calcium	is important for calculating the equilibrium pH value and ionic strength and, according to the scope of DIN 38404-C 10-R 2, is valid for values from 10 to 400 mg/l. Raw water with calcium ion concentrations outside this range is rarely encountered, but the calculation method can also be applied to deviating values.

Magnesium	This input is required for calculating "total hardness" (sum of alkaline earth metals), ionic strength and for calculating and checking electrical conductivity.

Acid capacity pH 4.3	is important for calculating the equilibrium pH value and ionic strength. Values outside the scope of DIN 38404-C 10 from 0.25 to 10 mmol/l are rarely found, but deviating values are also permissible.

Chloride	is required for calculating ion strength and is important for corrosivity, which is why the chloride value limits thickening. We recommend a limit of 250 mg/l, even in mixed installations, if suitable conditioning ensures good corrosion protection. The specified limit values of the manufacturers of systems and components should be observed for warranty reasons. Alternatively, different limit concentrations can be entered, e.g. the generally lower values of VDI 3803.

Sulphate	is required for calculating ion strength and is important for corrosivity and municipal wastewater discharge conditions due to its aggressiveness towards concrete; 400 mg/l generally limits thickening; alternative limit concentrations can be entered if desired.

Nitrate	is required for calculating ionic strength; if no measured value is available, it is not necessary to enter a value. A calculation is then performed (see above).

Calculated parameters:

Sodium	Anion-cation difference and, if applicable, conductivity difference (see above)

Electrical conductivity (25 °C)	(Not output in the raw water analysis output format); sum of the products of ion concentrations and equivalent conductivities; 1st correction according to Debye-Hückel-Onsager; see above; In circulating water, a second correction is also made by calculating the undissociated proportions of calcium sulphate and calcium carbonate using the complex formation constants in accordance with DIN 38404-10-R.

Forms of carbonic acid	The calculation of free carbonic acid, hydrogen carbonate and carbonate is based on DIN 38404-10-R 2 from KS4.3, pH value and the calculated thermodynamic variables.

Equilibrium pH value at TE	The calculation is performed in accordance with DIN 38404-10-R 2 and serves

Saturation index at TE	to characterise the raw water.

## 1.2 Window for entering the system	Cooling tower circuit
						Air scrubber

2.  Calculation of thickening and circulating water quality in the cooling tower circuit

The calculation is based on DIN 38404-10-R 2 / -R3 for characterising drinking water. The calculation is based on thermodynamic laws, in particular the dissociation equilibria of carbonic acid and solubility products. However, the pH value in the thickened cooling water cannot be measured. The carbonic acid concentration is required for the calculation. This is determined from the equilibrium setting at cooling tower water temperature TKT ( ) with the atmospheric CO2partial pressure (currently 0.41 0 /oo ). In addition, the equilibrium pH value (fictitious pH value at which the circulating water would be in calcium carbonate equilibrium) is calculated for the cooling water temperature in the cooling tower and the wall temperature TW. The difference gives the saturation indices. The saturation index at wall temperature SIW is a parameter that limits thickening.

2.1  Cooling tower circuit input mask

Enter the treatment type		Threshold stabilisation only (scale inhibition with corrosion protection)

Softening (with threshold stabilisation and corrosion protection)

Decarbonisation (with threshold stabilisation and corrosion protection)

Reverse osmosis after softening (with blending, threshold stabilisation and corrosion protection)

Reverse osmosis without softening (with blending, threshold stabilisation and corrosion protection)

Sulphuric acid dosing (with threshold stabilisation and corrosion protection)

Input of target and limit values		Maximum permissible SI:

Without conditioning, there is a tendency for calcium carbonate deposits to form at an SI > 0. SI values > 0 can be stabilised by dosing threshold inhibitors. Suitable combinations of threshold inhibitors enable SI values to be stabilised at around 3.0 under laboratory conditions. In continuous cooling tower operation, however, dirt particles are constantly introduced, which act as crystallisation nuclei, so that SI values > 2.5 are critical. In addition, low concentrations of iron ions cause interference. The recommendation of SImax= 2.3 takes into account an additional safety margin for changing operating conditions with fluctuations in raw water quality.

Maximum permissible chloride content:
Salts in general, as they cause electrolytic conductivity (a prerequisite for corrosion processes to occur at all), and chloride ions in particular, as they attack surface layers and promote material corrosion. The higher the chloride ion content, the greater the corrosiveness; therefore, there is no limit value in the true sense, but rather requirements for water quality with regard to the resistance of materials. The guideline values of 150 to 250 mg/l recommended by us refer to normal steel, alloyed steels and standard mixed installations in accordance with VDI 3803. With good conditioning measures and normal operating conditions, steel corrosion can be reliably limited to below 0.05 mm/a for these maximum values.

Maximum permissible sulphate content:
Corrosion behaviour as for chloride with a recommendation of max. 400 mg/l; in addition, a limit value generally of 400 mg/l (exception: 600 mg/l) applies to indirect discharge due to concrete aggressiveness.

E = 6
Limitation of the thickening factor with correction option; higher thickening is usually not advisable; the disadvantages of excessive contamination and excessively long retention times outweigh the advantages. If the circulating water is continuously cleaned in a partial flow by filtration, higher thickening factors are also possible. Any values > 1 can be entered.

Input of operating temperatures		Cooling tower temperature TKT
	This refers to the cooling water temperature in the cooling tower basin. It determines the content of free dissolved carbon dioxide in the cooling water, as according to Henry's law, equilibrium with the atmospheric CO2partial pressure is established there. The carbon dioxide content has a direct effect on the concentrations of all forms of carbon dioxide, pH value and SI.

Wall temperature TW
This refers to the highest wall temperature on the secondary side within this cooling system, as this is where the tendency for calcium carbonate to deposit is greatest. The SI limit value entered is based on this temperature. Approximate estimate: average of primary and secondary side temperatures. For oil coolers and water vapour: (see examples in the water manual).

##### Cost accounting		With a click of the mouse, you can choose whether to perform an operating cost calculation.

2.1.1. Threshold stabilisation		Based on the raw water analysis (E=1), this calculation programme increases the thickening factor E by 0.01 in a loop, multiplies the dissolved salts by E according to the analysis and performs all calculations again. The loop is run until one of the thickening-limiting parameters SIWmax  , Cl-max , SO4--max  or E = Emax   is reached. The permissible thickening factor E is then determined, for which all further calculations are performed.

	Note: In the circulating water, the pH values measured in the cooling water are often slightly lower than calculated. The reason for this is that the addition of feed water with a higher carbon dioxide content, usually discontinuously, increases the carbon dioxide content in the circulating water until it trickles down. However, since the feed is generally not continuous, the trickling down must be taken into account until equilibrium is reached.

2.1.2. Softening and threshold stabilisation

Blending	Feed water is blended water with a calcium content of 0.5 mmol/l (2.8 °dH); a different calcium hardness can also be entered via the "Limit values" input mask. This is used to calculate the blending ratio. In the case of very soft raw water with low hardness, a message is displayed indicating that softening is not necessary. The exchanged calcium and magnesium ions are replaced by sodium e ions. Caution! The feed water pipe should be as corrosion-resistant as possible. Thickening-limiting factors and calculation are then carried out as in 2.1.1 Threshold stabilisation. An open cooling tower circuit that is not designed to be completely corrosion-resistant should never be operated without hardness (see also VDI 3803).

2.1.3. Decarbonisation and threshold stabilisation

Intersection	SIW does not limit thickening in this case, but only Clmax , SO4 max  or E= E max  . E is calculated as for threshold stabilisation, but the degree of blending of completely decarbonised water with raw water is calculated by iterative approximation to the specified SI. Caution! The feed water pipe should be as corrosion-resistant as possible. For SImax , smaller values, e.g. 1.5, may also be entered, but the minimum alkalinity in the circulating water should not fall below 3 mmol/l KS4.3  due to increased material corrosion.

2.1.4. Desalination via reverse osmosis with softening and threshold stabilisation

Blending	Desalination is carried out by means of reverse osmosis. The thickening factor is always E = E max. The blending ratio of desalinated water with raw water is calculated by iterative approximation to the specified SI. Caution! The feed water pipe should be as corrosion-resistant as possible. Lower values may also be specified for SI and the maximum permissible chloride or sulphate content. With the same raw water analysis and the same boundary conditions, the same circulating water quality is calculated as in 1.2.1 Threshold stabilisation.

2.1.5. Desalination via reverse osmosis without softening and threshold stabilisation

Blending	Desalination by reverse osmosis can be carried out with softened water as feed water or with raw water and threshold stabilisation in the RO plant. The choice between the two processes affects operating and investment costs, but not the circulating water quality.

Input of SImax 	A maximum permissible SI must not be exceeded in the concentrate of the RO plant. For treatment in accordance with 2.1.5, it is therefore necessary to enter a limit value; recommendation: SImax  = 2.0. With suitably designed RO plants, a higher SI may also be permitted and recommended from an economic point of view.

2.1.6. Sulphuric acid dosing and threshold stabilisation

This process, also known as "internal decarbonisation", is still practised occasionally, although the associated increase in salt load inevitably leads to increased corrosivity. If the sulphate value is limited to 400 mg/l (observe discharge conditions!), this process is usually not economical. It also poses a considerable risk to operational safety due to the danger of overdosing. If the pH value is regulated, this must be done very precisely. A minimum alkalinity of 3 mmol/l in the circulating water is strongly recommended. Clmax , SO4 max  or E= E max   limit thickening, but SIW never does. The alkalinity in the circulating water is calculated at 4 mmol/l.

2.2. Correction of electrical conductivity	After each calculation of the circulating water quality at maximum thickening, the electrolytic conductivity is recalculated for all types of treatment. This is necessary because the permissible thickening is regulated by a limit value that must be set, and the conductivity is only approximately proportional at low salt content. First, the Debye-Hückel-Onsager correction is performed again. Then, partially undissociated portions of calcium sulphate and calcium carbonate are taken into account according to their complex formation constants. The incomplete dissociation of other salts is of minor importance and is not taken into account.

3. Calculation of thickening and water quality for air washers for room air humidification

The calculation is based on DIN 38404-10-R 2 / -R3, as for cooling tower operation. Instead of cooling tower and wall temperature, the water temperature in the air scrubber is entered.

3.1.  Air scrubber input mask

Input of the treatment type		Threshold stabilisation 
Softening
Decarbonisation 
Reverse osmosis after softening
Reverse osmosis without softening

Input of target and limit values		Maximum permissible SI:
The problem is similar to that encountered in cooling tower operation, but the sensitive areas are splash zones and droplet separators. Recommendation: SImax  < 2.0.

Minimum permissible hardness:
Unlike recooling plants, air scrubbers are often designed to be completely corrosion-resistant, so that no residual hardness is required. This value must be entered for ion exchange and reverse osmosis processes. 

Maximum permissible hardness:
The only guideline value, according to VDI 6022, is the permissible hardness of 7 °dH. Of course, different values can be selected depending on indoor air requirements, recommendations and manufacturer specifications. If the entered value is inevitably exceeded due to raw water quality and treatment type, a message is displayed with a note to check the input parameters.

Maximum permissible conductivity
Limitation depending on indoor air requirements and economic efficiency. Values < 1000 µS/cm are generally not mandatory, but should be aimed for.

Minimum alkalinity KS4.3
A minimum alkalinity must be entered for decarbonisation. This may also be below 3 mmol/l if the an e is corrosion-resistant. 

E = 5
Limitation of the thickening factor without correction option; higher thickening is not economically viable; the disadvantages of excessive contamination and excessive dwell times outweigh the advantages.

Input of operating temperatures		Air scrubber temperature TLW
For room air conditioning: water vapour saturated air at 12 °C corresponds to approximately 50% relative humidity at 22 °C).

##### Cost calculation		With a click of the mouse, you can choose whether to perform an operating cost calculation.

3.1.1. Threshold stabilisation		First, a check is made to see whether thickening is possible at all. Algorithm, as for recooling plant:  Based on the raw water analysis (E=1), E is increased by 0.01 in the loop and repeated until one of the thickening-limiting parameters SIWmax  , GHmax , LFmax  or E = 5 is reached. E is then fixed.

3.1.2. Softening and threshold stabilisation

Blending	Feed water is blended water of selectable hardness. This is used to calculate the blending ratio. The calculation is then performed as in 3.1.1. Threshold stabilisation.

3.1.3. Decarbonisation and threshold stabilisation

Blending	The minimum alkalinity in the scrubber water can be selected and determines the blending. For corrosion resistance, lower values than for RKW can be selected. Thickening limits are GHmax , LFmax  or E = 5. (Decarbonised feed water for LW is unusual and is usually only considered if it is available anyway).

3.1.4. Desalination via reverse osmosis with softening and threshold stabilisation

Blending	The calculation is identical to that for RKW with thickening-limiting parameters SIWmax  , GHmax , LFmax . E = 5 always applies. If the permissible maximum conductivity represents the thickening-limiting factor due to requirements or recommendations in air scrubber operation, reverse osmosis is usually the most economical process.

3.1.5. Desalination via reverse osmosis without softening and threshold stabilisation

Blending	Calculation as in 3.1.4.

Input of SImax	Concentrate calculation for the RO system is performed as described in 2.1.5.

4. Operating cost calculation input mask

Input parameters:

Municipal water costs	For calculating annual water costs. Also takes into account the water required to operate the pre-treatment systems.

Sewage charges	For calculating annual wastewater charges. Also takes into account the water required to operate the pre-treatment plants.

Energy costs	For calculating annual energy costs; only relevant for reverse osmosis, neglected for dosing, softening and decarbonisation.

Cooling capacity			Determines the amount of evaporation water per year;

Utilisation	Evaporation enthalpy at 30 °C is 0.6758 kWh/kg
1 kW evaporates approx. 1.480 l/h

Air scrubber capacity			Determines the amount of water evaporated per year.

Utilisation	3 g of water per m³ of air on an annual average for room air conditioning.

Dosing agent				To determine the annual operating costs for hardness

dosage level		stabilisation and corrosion protection; biocide treatment has no calculable connection to the type of treatment and is therefore not included in the cost calculation.

Salt tablets	Relevant for softening and reverse osmosis if a softening system is installed upstream. The salt requirement applies to ion exchange resin when using monospheric quality.

Hydrochloric acid	For calculating the annual operating costs for decarbonisation; basis: technical product 30–31% by weight. Quantity: equivalent to the exchanged alkalinity.

Sulphuric acid	For calculating the annual operating costs for sulphuric acid dosing; basis: technical product 98% by weight. Quantity: equivalent to the exchanged alkalinity.

Dosing agent RO			For determining the annual operating costs for hardness

Dosing level RO		Stabilisation during operation of the reverse osmosis system without softening.

4.1.1. Threshold stabilisation

Municipal water costs		Feed water quantity Z from wastewater quantity A + evaporation water quantity; A = V / (E – 1); 8760 h = 1 a;

Wastewater costs 		from wastewater volume

Dosing agent	Dosing agent quantity from dosing agent level (relative to circulation) * Wastewater quantity

4.1.2. Softening and threshold stabilisation

Municipal water costs			As in 4.1.1.; plus 5 l/l resin for regeneration and

wastewater costs			Rinse water for each regeneration;

Dosing agent				see above

Salt tablets	Resin capacity: 1.5 mol/l; 120 g salt/mol (full salting with monospheric quality and countercurrent regeneration)

4.1.3. Decarbonisation and threshold stabilisation

Municipal water costs			As in 4.1.1.; additionally 5 l/l resin for regeneration and

waste water costs			Rinse water;

dosing agent				see above

Hydrochloric acid				Resin capacity: 2.5 mol/l; hydrochloric acid quantity as equivalent

4.1.4. Desalination via reverse osmosis with softening and threshold stabilisation

Municipal water costs			As in 4.1.1.; additionally 5 l/l resin for regeneration and

wastewater costs	Rinse water; additionally, due to 80%  permeate yield for feed water production: 25% municipal and waste water, relative to feed water.

Rainwater drain	From version 3.0 (May 2002) onwards, it is also possible to calculate fees for separate wastewater streams. If concentrates from reverse osmosis plants can be discharged at reduced wastewater costs, this results in considerable savings potential.

Dosing agents				See above

Salt tablets				See above

Energy costs				1 kWh for 1 m³(not feasible for small systems)

4.1.5. Desalination via reverse osmosis without softening and threshold stabilisation

Municipal water costs	As in 4.1.1.; in addition, the permeate

wastewater costs 	yield depending on raw water quality and permissible SI; from this, the concentrate quantity is calculated.

Rainwater drain	From version 3.0 (May 2002) see 4.1.4.

Dosing agent				See above

Dosing agent RO			Enter the amount, based on concentrate

Energy costs				see above

4.1.6. Sulphuric acid dosing and threshold stabilisation

Municipal water costs			see above

Wastewater costs			See above

Dosing agents				see above

Sulphuric acid				Quantity as equivalent to displaced alkalinity

5	Additional programme options

5.1.	System information

The System info button allows you to display the required system components with the calculated output and a recommended price. This recommended price is also used to calculate the annual operating costs (depreciation, interest, maintenance). Version 4 is based on standard market prices for 2014.

5.2.1.	File ...

Save as: saves a project when a project name is specified.

Open: opens a saved project with all entries and calculations.

Import/export: imports/exports a project with all entries and calculations in Excel (.xls) table format.

Print: allows you to print a specified page on a selected printer.

5.3.	Edit Language

The programme can be used in several languages. Since 12/2008, the languages German, English, Danish and Polish have been available. An extension to other languages is possible at any time.

Copyright © Hartmut Kacirek, Nils Kacirek

06/2002

01/2005

01

February 2010

01/2012

12/2013

11/2014

06/2016 Last revised 05/2024